## Checkliste
Checklist for the minimum requirements for the reserve provider’s information technology for the provision of active power reserve (Version from 08/01/2018) The checklist must be completed and signed by the reserve provider and must be enclosed with the IT concept to facilitate and shorten the review by the TSOs.
2023-05-01
Company:
Firma:
Datum:
Freigabe erteilt
Freigabe nicht erteilt
Control reserve type
Contact person (with contact details)
Date
Erfüllt
Nicht Erfüllt
Teilweise erfüllt
Keine Prüfung
Rückfrage beim ÜNB
-
Information on the intended marketed power per LFR zone
Information on the intended maximum power of a technical unit (TU)
If necessary, information on the pool
No. | Category | FCR | aFRR | mFRR | Requirements | Reference reserve provider concept | Reserve provider comments | TSO comments
A01 | Availability | X | X | X ≥ 50 MW | The reserve provider’s central control system must be duplicated. A division into two redundant locations with regard to the infrastructure (communication and power supply) is targeted. The reserve provider must ensure the adequate security of its control systems for active power reserve. This requirement essentially also applies for aFRR, FCR as well as mFRR for a marketable power from 50 MW.
A02 | Availability | X | X | X | The operating location of the data centres used including staff must satisfy the EU’s legal requirements regarding data protection and comply with acknowledged techniques.
A03 | Operation | X | X | X ≥ 50 MW | An automatic switch between the reserve provider’s redundant central control systems must take place within a defined period. Product Maximum switch-over time aFRR 20 seconds FCR 15 minutes mFRR (≥ 50MW per LFR zone) 15 minutes
A04 | Network | X | X | X | The delay on the complete transmission route E2E (from the data logging by the technical unit through to the reserve provider control system and the receipt by the TSO) must take no longer than 5 seconds. A time stamp (stamped on the left or right) is generally required. The requirement applies for aFRR. Similar times must be targeted for FCR and mFRR. The reserve provider specifies the maximum delay time.
A05 | Network |  | X ≥ 50 MW |  | Reserve providers whose marketed aFRR within an LFR zone amounts to 50 MW or more must continue to realise the connection between the TSO and the reserve provider’s control system with the current point-to-point fixed-line connection (SDH/PDH) or equivalent technologies (see the definition in Annex 2, chapter 5 on the requirement for closed user groups for providing active power reserve). This requirement also applies for reserve providers who intend to market 50 MW or more aFRR in the future.
A06 | Network | X ≥ 90 MW | X ≥ 50 MW |  | Reserve providers whose marketed CP is 50 MW or more must operate the control system with a local redundancy (see the glossary and annex “Notes concerning the spatial separation between redundant data centres”). Reserve providers who are targeting a marketable power of 50 MW or more per LFR zone should note that the implementation of this requirement is a prerequisite for marketing higher power (≥ 50 MW). The requirement applies for aFRR. A local redundancy should be targeted for FRC and mFRR. If the central control system is required for the compliant provision of the FRC (e.g. for battery management), the control system must have a locally redundant design from a marketable power ≥ 90 MW.
A07 | Network | X | X | X ≥ 50 MW | The connection of the control technology to provide active power reserve must take place in the form of a dedicated point-to-point connection between the TSO’s control centre and the reserve provider’s control system. This can be realised by classic fixed-line connections or new technologies. Solutions based on the Internet as the medium are excluded between control systems. This requirement also applies for mRFF from 50 MW of marketable active power reserve (also refer to chapter 3.1.2.3).
A08 | Network | X | X | X | Serial interfaces (V.24/V.28) with IEC protocol 60870-5-101 (TSO-specific) must be used. In consultation with the TSO, X.21 instead of V.24 can be used as the interface format.
A09 | Network | X | X | X | If the reserve provider operates control systems with local redundancy, these must be redundantly connected to the TSO’s control system at the TSO’s request (potentially with additional redundancy to the TSO’s two transfer points (see A11)).
A10 | Network | X | X | X | With regard to the use of Internet technologies (not to be confused with the use of the public Internet excluded under A07), the basic requirements in chapter 3.1.2.3 must be observed.
A11 | Network |  | X |  | The transmission routes and interfaces to the TSO’s two transfer points must have a completely redundant design in relation to one another: • node and edge disconnected, • no double use of devices and • no double use of cable routes.
A12 | Availability | X | X | X | The individual connection between the TSO’s and reserve provider’s control systems must at least have an availability of 98.5% (arithmetic total availability of both connections is 99.9775%). The requirement applies for aFRR. Similar availabilities must be targeted for the FCR and mFRR. The reserve provider nominates the availability per transmission path.
B01 | Closed user group | X | X |  | Only closed user groups are permitted in the access networks for the participant connection. The communication between the TU and control systems must be strictly shielded from other networks (e.g. Internet, networks of other customers or service providers) by using closed user groups. The closed user group should only use private addresses, which cannot be accessed by other networks. The TU should not be able to communicate with one another, but rather exclusively via the central gateway to the reserve provider’s control system.
B02 | Closed user group | X | X | X | The closed user group is exclusively used to provide control reserve. Additional data, which is related to the provision of system services, may be permitted in consultation with the TSO connecting to the reserves (e.g. for the following services: SNMP for monitoring the connected devices, NTP for central time synchronization, configuration updates). All other IT services must be disabled. Only the participants required for the provision of the control reserve, such as the reserve provider’s control system or the reserve provider’s prequalified TU, may be included in a closed user group. In particular, the following systems must not be operated within the closed user group: • downstream IT systems of the TU operator, • Office IT systems of the reserve provider or manufacturer and • IT systems of other reserve providers (relates to SaaS providers).
B03 | Closed user group | X | X | X | The use of Internet technologies (e.g. IP, xDSL, UMTS, LTE) is only permitted when using a closed user group established exclusively for this purpose and provided by the telecommunications provider. A closed user group established by the telecommunications provider must ensure that the reserve provider’s network traffic does not come into contact with “external” networks. The traffic should therefore be secured from the telecommunications provider’s other networks, e.g. from other customer networks or the Internet.
B04 | Encryption | X | X | X | Within the closed user group, the reserve provider must establish a separate end-to-end encryption (not by the telecommunications provider) to additionally secure the communication between the TU and control systems with the closed user group’s network.
B05 | Encryption | X | X | X | The data transferred between the access routers must be transmitted via an encrypted tunnel with an IPsec VPN or OpenVPN, with AES256 or Wireguard VPN, respectively. A recommendation for a secure encryption is described in Annex 3 (Requirement for closed user groups for the provision of control reserve).
B06 | Closed user group | X | X | X | From a configuration perspective, only other connections within this user group may be reached by a connection within a closed user group. A direct connection to the Internet or the availability of public IP addresses on the Internet or other user groups is therefore excluded. This requirement also includes access points for external service providers and other locations. Communication via VPN or site-to-site connections, which do not belong to the closed user group, is prohibited.
B07 | Network | X | X | X | The access router must be configured such that all network traffic is routed to the VPN tunnel. Communication outside the tunnel (except to establish the tunnel) is prohibited (including for administration and monitoring).
B08 | Network | X | X | X | Automated, cyclical monitoring of the router configuration with an integrated alert function (SMS, email) must be ensured. A daily or at least weekly check should prevent any prohibited manipulation of the router.
B09 | Closed user group | X | X | X | The reserve provider is responsible for applying for a connection and a closed user group with the telecommunications provider. The associated contract must be concluded between the reserve provider and the telecommunications provider. Contracts where the telecommunications provider grants itself the right to temporarily interrupt the connection on a regular basis, e.g. after 24 hours, must be excluded.
B10 | Network | X | X | X | The reserve provider is obliged to only select telecommunications providers that promptly inform the reserve provider of planned maintenance work in advance. Irrespective of this, the reserve provider must take precautions for this case in order to meet its obligations to provide active power reserve (e.g. via redundant connections or suspension of marketing).
B11 | Encryption | X | X | X | All transmission routes must be encrypted. This requirement does not affect point-to-point connections with a serial design. These do not require any encryption.
C01 | Availability | X | X | X | Every TU must be connected to the reserve provider’s control system with an availability of the individual connection of at least 95%. (Evidence can be provided by contracts, by the system or via statistics). If the reserve provider operates locally separated control systems based on requirement A06, the TU is connected to each of the two control systems (potentially also redundant per control system as per C02 / C03).
C02 | Network | X | X | X | TU with power ≥ 30 MW aFRR must also be redundantly connected to the reserve provider control system. This requirement must be targeted for TU that provide mFRR or FCR.
C03 | Network |  | X ≥ 50 MW |  | TU that provide 50 MW aFRR or more must continue to be connected with the existing, redundant point-to-point fixed-line connection (SDH/PDH) or equivalent technologies (see the definition in Annex 3, chapter 5 on the requirement for closed user groups for providing active power reserve).
C04 | Network | X | X | X | The TU must be connected via a serial interface. A media break to the Internet protocol (IP) is mandatory. Alternatively, the direct control of TU via binary or analogue outputs (e.g. switch actuators) as well as the direct recording of measured values using binary inputs or AD converters is also permitted.
C05 | Network | X | X | X | Concept for bundling of small TU • Bundling of small TUs via public Internet with encrypted VPN is allowed. • For bundling of small TUs, closed user groups are not obligatory. • If small TUs are bundled via the Internet, the provider must demonstrate, e.g. by means of a penetration test, that the bundling is operated securely in accordance with the state of the art. • A serial interface must be implemented as a media break between bundled small TUs and the pool operator in accordance with IT requirements. • The installed capacity of a small TU may not exceed 100 kW. • The marketed capacity of a bundle of small TUs may not exceed 10 MW. • The connection of a micro-installation is only permitted to a pool (no multiple sales possible). • The collateralization of a bundling of micro-installations by a different bundling of micro-installations is not permitted if the prerequisite for the secured provision and the provision of control reserve is an intact communication technology connection. • Within a bundling of small TUs, no small TUs for outage backup can be used. However, this outage backup cannot compensate for the outage of the entire bundle. • Within a bundling of small TUs, an aggregation of small TUs is allowed, which are then integrated in the bundling of small TUs, as long as the maximum marketed capacity of the bundling of small TUs is not exceeded. Each aggregation can only be connected to a bundling of small TUs via internet using VPN. This aggregation only applies to the communication channels, not to the data points. • The requirements from D02 (fault clearance within 24 hours) do not apply to individual small TUs, but to the entire bundle of small TUs.
C06 | Network | X | X | X | Bundling of power plants (generators and/or consumers) at a common grid connection point • TUs, which are connected via a common network connection point, can be understood as one TU in the sense of this IT concept. For this bundling, only one communication link to the provider control system is required. • The redundancy requirements from C02 and C03 must be considered accordingly. • These bundled power plants are treated as one TU for collateralization purposes. • Within the bundling of systems, own networks without public Internet must be used. • The use of the serial interface according to C04 is still required.
D01 | Network | X | X | X | Data transfers from and to other networks with a different protection requirement essentially take place with data hubs. Data hubs ensure that data can be transferred between the network used to provide the active power reserve and the other networks with a lower protection requirement without establishing a direct connection between these networks. • Only unidirectional communication from the control system is permitted, i.e. data can only be exported or retrieved from the control system’s network. • Exclusive use of SFTP or comparable, encrypted protocols. • Multi-stage virus protection on the data hub.
D02 | Operation | X | X | X | Faults on parts of the overall system without a complete failure, i.e. without impairing the provision, must be rectified by the reserve provider within 24 hours after the occurrence of the fault. If the fault does not occur on a working day, troubleshooting on the next working day is considered adequate.
D03 | Operation | X | X | X | The reserve provider must ensure the continuous and seamless monitoring of the availability of the transmission paths, including all CPE.
D04 | Other | X | X | X | Adequate access protection to the premises, systems and networks, which are required to provide the active power reserve, must be ensured (e.g. access and key concepts, authorisation management and physical security measures in connection with adequate instructions and checks). Electrical operating rooms must be locked. The reserve provider’s devices must also be housed in a sealed safety cabinet secured by an alarm.
D05 | Other | X | X | X | The reserve provider must operate an integrated patch and change management, demonstrate this as part of the pre-qualification and document the relevant processes. Updates are transferred via the data hub principle (see D01) independent of the type of system to be updated (operating system, application, virus signatures, etc.). In this case, the data are always retrieved by the servers located in the secure zone. The data are therefore reviewed on every system (e.g. for malware, standard conformity and plausibility).
D06 | Verifications | X | X | X | All measures (technical concept, routing, fault clearance times, maintenance contracts, etc.) to achieve the required availability must be presented to the TSO upon request.
D07 | Operation | X | X | X | If technologies are compromised, the reserve provider is required to notify the TSO. If the TSO becomes aware of a compromised technology, the reserve provider must repair the compromised technology upon request. In this case, alternative technologies must be implemented within a transition period arranged with the TSO.
D08 | SaaS | X | X | X | Reserve providers that procure services from external IT service providers that, in turn, offer their services to several reserve providers (e.g. SaaS providers) are subject to special regulations: • The procurement of services from the aforementioned IT service providers must expressly be disclosed as part of the pre-qualification and approved by the TSO. • Reserve providers that procure these kinds of services are essentially treated as reserve providers with the highest protection requirements (as per aFRR ≥ 50MW). • IT service providers that provide services for various reserve providers and their associated reserve providers must ensure that the operation of jointly used components does not present any risks for other reserve providers. For example, only one reserve provider may be connected per closed user group. • The reserve provider is the main contact partner for the TSO and bears overall responsibility for fulfilling the IT requirements to provide active power reserve.
3.2 | Verifications | X | X | X | The reserve provider must verify the security of its overall E2E system (bidirectional data exchange between the technical unit to the TSO via the reserve provider control system) as defined in chapter 3.3. The following requirements must be ensured: • The reserve provider must verify the technical contractual content on IT security and availability with the TSO or a commissioned third party (for example, this can take place in the form of an inspection of the relevant text passages for existing contracts). • The reserve provider must demonstrate the existing risk or basic protection analyses with the TSO upon request. • The reserve provider must demonstrate the conceptual planning and implementation of IT security measures with the TSO upon request (potentially also on-site). The reserve provider must immediately notify the TSO of security-related changes and security incidents in the overall system. o Security-related changes may include: Changes to the configuration of the VPN tunnel, change of the router hardware model, conceptual changes, etc. o Security incidents include: Awareness of weaknesses in the router configuration or router firmware, unauthorised third-party access, attacks on the access router or downstream systems, etc. • The reserve provider must immediately inform the TSO if the data provision to the TSO cannot be properly ensured. • The reserve providers must record the following information to check the reliability and report to the TSO, particularly in case of an error or upon request: o Frequency and duration of the faults o Causes of the faults o Switch-over time to redundancy connection o Time until the rectification of the faults o Affected measures to restrict and eliminate the fault o Measures to prevent the error in the future • The TSO communicates changes to the IT requirements on the internet platform regelleistung.net to the providers accordingly. • If necessary, the concepts must be adapted accordingly by the reserve provider in consultation with the TSO. • Changes to the IT concepts must be presented to the connecting TSO for review before the start of implementation. • To support a regular adaptation of the IT requirements, the provider is asked to provide an annual report on the operation of the RL-IT systems to the relevant connection TSO on 31/01 for the previous year (see Annex 3 “Report on the provider’s information technology and incidents while providing control power).
3.3 | Verifications | X | X | X | The reserve provider confirms, within the scope of self-disclosure (see below) and verifications (see chap. 3.2), that the existing minimum requirements for the reserve provider’s information technology for the provision of control reserve are complied with. The self-disclosure must be signed by the managing director or an authorised representative of the reserve provider. As part of the pre-qualification, the reserve provider must submit the following documents to check the IT requirements for providing control reserve: • Submission of a comprehensive IT concept (without specification of any operational relevant information such as an IP address) • IT checklist with assignment of the corresponding chapters of the IT concept including the description of the encryption technology as well as a list of the involved telecommunication service providers or Software as a Service providers (see Annex 1: Checklist for the minimum requirements for the reserve provider’s information technology for the provision of control reserve). • Classification of the information security of documents submitted by the provider. Changes to the IT concepts (even without impact on the prequalified service) must be submitted to the TSOs for approval prior to use. Reserve providers, service providers for the provision of control reserve and IT system service providers that bundle units or systems for the control and bundling of generation and consumption equipment with a net nominal output of at least 104 MW (36 MW in the case of prequalification for the provision of primary control reserve) in Germany are subject to mandatory certification in accordance with BSI-KritisV 2.0 as from 14/09/2021. In this case, verification is required by way of a certification pursuant to the provisions of the BSI, the IT Security Acct and BSI-KritisV as well as based on the IT security catalogue in accordance with Section 11 (1a) EnWG or pursuant to an IT security catalogue in accordance with Section 11 (1b) EnWG. As was already the case in the consultation version of this document from April 2018, the TSOs do not require a mandatory certification of all reserve providers until further notice. The requirements described above are legally prescribed minimum requirements, which provide for a certification obligation from an installed nominal capacity of 104 / 36 MW (electrical).

## VPN
Detailed information on the VPN configuration
Company:
Firma:
Datum:
Freigabe erteilt
Freigabe nicht erteilt
Control reserve type:
Contact person (with contact details)
Date:
| VPN technology | Category | Selection of the reserve provider
1 | IPsec/IKEv1
1.1 |  | Confidentiality of information
1.2 |  | Authentication of the communication partner
1.3 |  | Protecting the integrity of a message
1.4 |  | Protection from replaying old messages
1.5 |  | Perfect Forward Secrecy
1.6 |  | Refreshing key material (re-keying)
2 | IPsec/IKEv2
2.1 |  | Confidentiality of information
2.2 |  | Authentication of the communication partner
2.3 |  | Protecting the integrity of a message
2.4 |  | Protection from replaying old messages
2.5 |  | Perfect Forward Secrecy
2.6 |  | Refreshing key material (re-keying)
3 | OpenVPN
3.1 |  | Confidentiality of information
3.2 |  | Authentication of the communication partner
3.3 |  | Protecting the integrity of a message
3.4 |  | Protection from replaying old messages
3.5 |  | Perfect Forward Secrecy
3.6 |  | Refreshing key material (re-keying)